stop gates

1. General
	1. scope of work

This section covers stainless steel or aluminum stop gates sealing on 3 sides, designed for operation by hand or with lifting equipment. The contractor shall furnish all labor, materials, equipment and incidentals required to install and field test the gates shown on the Contract Drawings and specified herein.

* 1. References
		1. Definitions

Design Head: The maximum differential head that will be applied on the gate under worst case conditions, measured from the gate invert. Design head shall be equal to the height of the slide.

Seating Head: Head applied on a wall mounted gate, in the direction that pushes the gate against the wall it is installed on.

Unseating Head: Head applied on a wall mounted gate in the direction pulling the gate away from the wall it is installed on.

Operating Head: The highest differential head that is to be applied on the gate when it needs to be operated, measured from the gate invert.

* + 1. Reference Standards

ASTM A240/A240M – Standard Specification for Chromium and Chromium Nickel Stainless Steel Plate, Sheet and Strip for Pressure Vessels and for General Applications.

ASTM A276 – Standard Specification for Stainless Steel Bars and Shapes.

ASTM A582/A582M - Standard Specification for Free-Machining Stainless Steel Bars.

ASTM D2000 - Standard Classification System for Rubber Products in Automotive Applications.

ASTM D4020 - Standard Specification for Ultra-High-Molecular-Weight Polyethylene Molding and Extrusion Materials.

ASTM F593 - Standard Specification for Stainless Steel Bolts, Hex Cap Screws, and Studs.

* 1. Submittals
		1. Drawings

The slide gates manufacturer shall submit, for acceptance by the purchaser, general arrangement drawings of the equipment supplied under this section. Drawings must indicate all dimensions that will allow the contractor to ensure coordination with dimensions of the installation environment. Drawings will also show sufficient details to determine compliance with the requirements, including the plate thickness used for all components.

* + 1. Installation, Operation and Maintenance Manual

The gate manufacturer shall provide a manual containing the instructions for installation, operation and maintenance of the slide gates. The manual shall also contain the detailed information on the terms of the 5 year warranty on the products.

* 1. Quality assurance
		1. Qualifications

The gates supplied under this section shall be standard products of a manufacturer regularly engaged in the design and manufacturing of water control gates. The specifications are based on FONTAINE-AQUANOX Series 92 Stop Gates manufactured by ISE Metal Inc.

* + 1. Standards and Certifications

The stop gates manufacturer must maintain an ISO-9001 certification and also a company certification for its welding operations from the CWB or AWS.

* 1. Delivery

The manufacturer shall use due and customary care in preparing the gates and accessories for shipment. When shipping several gates together, every item shipped separately must be clearly marked to the gate it belongs to.

* 1. Warranty

The stop gates and accessories shall be covered by a five (5) year warranty from the manufacturer against defects in materials, design and workmanship. The warranty period will start from the date of delivery of the equipment to the installation site.

1. Products
	1. Equipment
		1. Manufacturers

Gates supplied shall be FONTAINE-AQUANOX Series 92 Stop Gates, as manufactured by ISE Metal Inc. or approved equal.

* + 1. Description

The gates shall be upwards opening of the 3 sides sealing type designed for water or wastewater applications.

* + 1. Performance and Design
			1. Slide

The slide consisting of a flat plate with welded reinforcing ribs shall be designed to withstand the design head specified in the gate schedule with a maximum deflection of 1/720 of the gate opening width and with stresses in the slide limited to 25% of the ultimate tensile, compressive, and shear strength and 50% of the yield strength, whichever is less. Minimum material thickness of all members of the slide shall be ¼ in (6mm).

* + - 1. Frame

The stainless steel frame having a U-shaped form is acting as a guide for the slide. The gate frame shall be constructed of structural members or formed plate. The frame shall be suitable for mounting on a concrete wall (CW) at the end of a channel, embedded inside a channel (FE) or mounted on a channel surface (EC). The frame configuration shall be of the flush-bottom type. The bottom of the frame will be of the flush invert type. Minimum material thickness of all members of the frame shall be ¼ in (6mm).

* + - 1. Guiding, Seating and Sealing

Side seals shall be made in EPDM and composed of a lip seal on both sides, preventing flow in both directions. The side seals shall be retained to the slide using UHMWPE guide bars and screws. The guide bars acts as gliding seats in order to ease the positioning of the slide in the frame and to reduce friction. Seals shall limit the leakage rate below the maximum in both seating and unseating conditions. The bottom seal shall be set into the bottom frame and shall form a flush-bottom.

* + - 1. Leakage

The Series 92 stop plates shall be substantially watertight under the design head conditions. Leakage shall not exceed 0.1 U.S. gallon per minute per foot (1,25 l/min per meter) of seal periphery under the design seating or unseating.

* + 1. Anchor Bolts
			1. The quantity, size and location of anchor bolts shall be determined by the gate manufacturer and shown on the submittal drawings.
		2. Materials

|  |  |  |
| --- | --- | --- |
| Frame | Stainless Steel | ASTM A240, grade 316L or 304L |
| Slide | Stainless Steel or Aluminum | ASTM A240, grade 316L or 304L or Aluminum ASTM B-308 - Alloy 6061-T6 |
| Guide Bars | Ultra High Molecular Weight Polyethylene (UHMWPE) | ASTM D4020 |
| Side Lip Seals | Ethylene Propylene (EPDM) | ASTM D2000 |
| Flush Invert Bottom Seal | Ethylene Propylene (EPDM) | ASTM D2000 |
| Wall Gasket (if CW mount) | Ethylene Propylene (EPDM) | ASTM D2000 |
| Bolts and Hardware | Stainless Steel | ASTM F593, grade 316 |

1. Execution
	1. InstallATION
		1. It is the responsibility of the Contractor to handle, store and install the gates in strict accordance with the manufacturer’s instructions and recommendations. The Contractor shall review the installation drawings and instructions before proceeding to the installation of the gates.
		2. The gate assemblies must be installed on a true vertical plane, square and plumb.
	2. FIELD TESTING
		1. After installation, the gates must be field tested by the Contractor, in the presence of the Engineer and Owner, to ensure compliance with the requirements of these specifications. Each gate shall be operated on its complete open-close cycle to confirm proper operability.
		2. Each gate shall be water tested by the Contractor and sealing performance shall be observed.

**stop GATES SCHEDULE**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | ID TAG | Qty | SIZE (W x H)(inches) | DESIGN HEAD (ft) | FRAMEMOUNTING |  |  |  |  |
|  |  |  |  | Seat. | Uns. |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |

**Abbreviations:**

FRAME MOUNTINGS:

 CW: Mounted on a concrete wall at the end of the channel

 FE: Embedded inside the channel side walls (grouted in box-outs)

 EC: Surface mounted onto the channel side walls (grouted)

End of Section